## Slide 1: Cryogenic Controller SW Toolkit (PLC Library)
Dan Popovic

## Slide 2: What is Cryogenic Controller Toolkit?
Set of FBs for control of standard ESO cryogenic system components.
Based on EtherCAT technology and Beckhoff PLCs.
Provides control solutions for common components and subsystems as defined in Vacuum and Cryogenics Standard Components, ESO-046147 Version 6
The toolkit does not provide a control system.
Design and safety are responsibility of the designer.
Examples of control systems and subsystems based on the Toolkit are available.
They can be used as the starting point for new Cryo projects.

## Slide 3: SW Toolkit Overview

## Slide 4: Cryo Related PLC Libraries
cryo.library // Cryo components FB_CRYO_*
cryohmi.library // Interface to HMI FB_HMI_CRYO_*

## Slide 5: SW Toolkit Components
Analog sensors – temperature, pressure, flow
Valves
Pumps
Coolers and Compressors
Heaters
Evacuation systems (currently only 50L and 50,000L)
Lakeshore (rsComm* libraries)
etc.
Note: Components are OPERATIONAL on boot!

## Slide 6: in_bEnable Concept
in_bEnable input parameter is used to control components, e.g., ON/OFF, OPEN/CLOSE, START/STOP, etc.
Control loops can be disabled, e.g., heater during evacuation.

## Slide 7: TwinCAT Analog Sensor Process Data

## Slide 8: Analog Sensors

## Slide 9: FB_CRYO_SENSOR_TEMPERATURE
Provides temperature in C and K
Provides temperature ramp
By default, Beckhoff supports PT100 temperatures down to -200 C.
By reading resistance (in_bResistor_1_64 = TRUE), range extended down to -240 C.
CoE 0x80n00:19 "RTD element“ must be set to “Resistor 1/64 Ohm”.

## Slide 10: FB_CRYO_TEMPERATURE
Supports two temperature sensors
Takes first Valid reading

## Slide 11: Pressure Transducers Conversion Curves
Configurable pressure transducer type
TYPE E_CRYO_SENSOR_TYPE_PRESS :
(
NONE := 0,
PKR_250 := 1, // Pfeiffer PKR250 & PKR251
CMR_361 := 2, // Pfeiffer CMR361
WRG_D_NW25 := 3, // Edwards WRG-D-NW25
PKR_360 := 4 // Pfeiffer PKR360
);
END_TYPE
Built-in Volt-to-Pressure conversion

## Slide 12: FB_CRYO_SENSOR_PRESSURE
Configurable sample time for averaging, e.g., every 3 sec.

## Slide 13: FB_CRYO_PRESSURE_VOTE
Supports up to five pressure sensors
Configurable voting system
TYPE E_CRYO_VOTE :
(
V_AVE := 0,
V_MIN,
V_MAX,
V_1oo2,
V_2oo3,
V_3oo5
);
END_TYPE

## Slide 14: Pressure Voting Logic – X out of Y

## Slide 15: FB_CRYO_BIN_ACT – Binary Actuator
Simple digital ON/OFF actuator used in binary controllers: valves, heaters, etc.
Feedback: ON_ONLY or ON_AND_OFF.

## Slide 16: FB_CRYO_BIN_CTRL – Binary Controller
Includes an actuator.
M_GetStateLabel() sets labels, ON/OFF, OPEN/CLOSED, etc.

## Slide 17: Binary Controller State Machine
Controller can be disabled.

## Slide 18: Pumps
Supported models:
ECODRY PVP
MVP030 PVP
HIPACE30 TMP
ATH2303M TMP
More to come…

## Slide 19: Pump GUIs

## Slide 20: Coolers and Compressors
Supported models:
Cryotel GT
CRYOMECH CPA289C

## Slide 21: FB_CRYO_CMD_OVERRIDE – Command Override
FB_CRYO_CMD_OVERRIDE
Mode:
AUTO
MANUAL
ENG
Function
e.g. Valve
GUI_CMD_OVERRIDE
Function Ctrl Mode
System Cmd
Active Cmd
System Interlock

## Slide 22: Command and Sensor Override GUI Examples

## Slide 23: Evacuation Systems
Supported systems: up to 50L (PDS) and up to 50,000L (MICADO) cryostats

## Slide 24: Cryo Controller System - Example

## Slide 25: Cryo System Control Cycle
M_ReadSensors(); // Read Temperatures, Pressures, Flow, etc.
M_CheckForSensorErrors(); // Check for sensor HW errors
M_ExecuteControllers(); // Execute Controllers, e.g., valves, pumps, etc.
M_CheckForCommands(); // Capture system commands , e.g., warm-up
M_SafetyCheck(); // Perform a safety check
M_ProcessTriggers(); // System logs, e.g., in vacuum, cold, etc.
M_ProcessHmi(); // Provide information to HMI
M_StateMachine(); // Execute system state machine

## Slide 26: Logs and Alarms
Every Device FB provides Logging and Alarm handling.
Implemented in Type System / Event Classes.

## Slide 27: Logs and Alarms – Output Example

## Slide 28: Simulation Helper FBs
FB_CRYO_SIM_BOOL_DELAY // Delayed reply of actuator with single feedback
FB_CRYO_SIM_BOOL_DELAY_2 // Delayed reply of actuator with ON/OFF feedback
FB_CRYO_SIM_LREAL // Ramp, sine, curve
FB_CRYO_SIM_SINE // Simple sine wave generator
FB_CRYO_SIM_PRESSURE // Ramp, curve
FB_CRYO_SIM_TEMPERATURE // Ramp, sine
Examples of customized subsystem simulations - FB_SIM_MICADO_PUMPS - FB_SIM_MICADO_VALVES - …

## Slide 29
@ESOAstronomy
@esoastronomy
@ESO
european-southern-observatory
@ESOobservatory
Dan Popovic – dpopovic@eso.org